ATTN: Kush

Here is the breakdown of what needs to be done with the boilers at address 532 west 42nd st, Manhattan, NY

3 Boilers, all having issues that originate from no combustion set up. Improper or no combustion setup creates a variety of problems, such as too much gas entering the coil chamber (creating warps in the stainless cover, blowing  gaskets, contaminating the coil, too slow airflow from blower (creates a buildup of high flue gases unable to leave properly causing too much heat to build up in the chamber and blow gaskets, damage the fire proofing cookie and warp the casing).

All damage done to units show that no set up appeared to be done.  Melting ignitor sensors, blown gaskets, warped top cover, damage fire proofing, contaminated and damaged coils and high buildup of moisture and C02 inside the unit casing.

Unit #1 (first unit when entering room) serial # h08195949

Unit has a damaged coil, can see flame from inside coil from blown gaskets, damage done from contaminated and blocked coils, forcing the heat and exhaust to escape out the gaskets instead of the exhaust venting.  Recommend Just the coil on this unit, everything else on it appears to be working- But that does not mean there is no damage already done to the parts still working, such as ignitor wear, moisture hitting the blower control board.  Price to fix unit - Coil heat exchanger (we also include the gaskets and freight) - $3,329.00 + $600.00 Labor + $150.00 Combustion set up. Complete installed $4,079.00

Unit #2 (Right of first unit) serial #H08195561

Unit appears to be in best condition of the bunch although appears to be having issues with Lock Out code. May of just been a fault control board, (replaced control of unit with the control from unit #3). Unknown if unit has any other issues since it was running improper all this time, but would recommend a better examination of coil chamber once unit #3 is working just to ensure, as sometimes checking the coil can cause parts of the fire proofing to collapse on a already damaged coil.  Just keep in mind the control board used was a used one from unit #3.

Unit #3 (last in room) H08194648

Unit damaged from no combustion set up. Top of coil chamber is warped and gaskets are blown out coil is also blocked, causing excess gas C02 and moisture to leak into boiler casing, damaging the electronics.  Unit needs a new coil- But also needs a new control (as we used the control on unit #2 to get it running) Unit also needs a blower and ignitor.  Blower when removed had water in it.  (if customer wants to try to salvage old blower we can try, and deduct it from complete installed package price)

Price to fix unit - Coil heat exchanger (we also include the gaskets and freight) - $3,329.00 + Blower $795.00 + Control board $670.00 + Ignitor $170.00 + $600.00 Labor + $150.00 Combustion set up.

Complete installed $5,714.00

All our work comes with a 1 year warranty on the work that we do (this includes only our parts which we bought and installed) We can not warranty any parts not replaced or bought elsewhere.   We are also backed by the manufacturer on the repairs and warranty work done by us. Laars heating systems.

Coils come with a new factory warrenty on them of 5 years + 5 years pro rate. (warranty on coils are void if improper installation is issue of damage dealt, such as no combustion setup.)

Keep in mind, a lot of damage has been occurring over the years with these units with the exhaust leaking back into them, and may at some point need to replace the electronics such as a board or blower on any of them that have not been changed by us, so we can not say that nothing else will break down but we cover the work we have done and the parts we have replaced.

A service call fee of $275.00 to troubleshoot and find the problems of the units Will be waived if any work to replace a coil is done.

A deposit will be required to place the order for the coils, can take a few days to get coils in.