Siedle Programming Notes  9-27-22

Our system has two separate buses for the locks; one for the elevator locks and one for the entrance locks. 
To program elevator locks, you need to plug into the USB programming interface in the far right siedle box.
To program door locks, you need to plug into the USB programming interface in the box above the washing machine area. 
So to add a fob or fobs you need to add once at the elevator box and again at the washing area box.

USE the VARIO software to program the locks.
When prompted enter the password for the INSTALLER, "Siedle".
Plug the printer end of the cableinto the programming interface and the other end into the pc running the software USB interface.
You must enter the code 5345 in the module in the respective box:
Open the module flap
press OK
use up arrow to enter each digit followed by right arrow after each digit
press OK
Hit CONNECT on the vario software
Hit READ and first read the DEVICE list
Hit READ and read the EC ELM settings
If you are programming FOBS, hit READ CARDS at the bottom.
For the elevator, there is only ELM from which to read.  Others are greyed out.
For the doors, there are two choices, one for each ELM in  front and in the lobby.  #2 is the one in the vestibule and is more convenient to read the cards.
Hit START CARD READ IN and it will show ready in the message box to the right and the ELM will have green and red led lights lit.  
Pass the fob in front of the ELM and the green LED will flash.
Back at the software interface, the new fob id will show up. 
CLICK the appropriate boxes for which floors or which doors to open.  
For doors, you will CLICK both boxes.
Repeat for other fobs.
Click FINISHED READ IN.
Write the new file back to the system.
SAVE the file.
Hit DISCONNECT.
Disconnect the USB cable.
Test the Fob or fobs.
1. Opens doors
2. Opens appropriate floors
3. Opens 9
4 Does NOT open any other floor.

* I had trouble connecting and reading in the elevator.  I reconnect the wires. I must have shorted them because all the modules went blank.  I found the fuse blown over in the washing area junction box in the transformer module.  Its 400ma 250V glass mini fuse. I bought some extra fuses and have them in the module and in the siedle supplies area in the credenza.